## PV Panels - Electrical Design
Designing with Comtec Energy PV Panels
Note : Select "Grey" cells & Enter Data in "Yellow" ones |  | Remarks
Panel Model | CEP-250M-60 | Select Comtec Energy Solar Panel Model Here
Panel Wattage | 250 | Specification & Type of your Selected Panel
Panel Type | Mono
Panel Voc | 38
Panel Vmp | 30.5
Panel Imp | 8.2
Panels in Series per String | 20 | Enter number of panels in series (string)
Strings per Array | 1 | Enter Number of Strings
Number of Arrays | 1 | Enter Number of Arrays
Total Number of Panels | 20 | Number of Panels and Total PV in Wp
Project PV size | 5000
Site Temperature (LO - min) | -10 | Enter minimum temperature of site in a year
Site Temperature (HI - max) | 52 | Enter maximum temperature of site in a year
Max Increase in Voc @ min Temp | 11.9%
Max decrease in Voc @ max Temp | 9.18%
LO Temperature Compensated Voc | 42.522
HI Temperature Compensated Voc | 34.5116
Voc - Array - Non-TempCompen | 760
Voc - Array - LO Temp Compensated | 850.44 | Use this Voc value as max OC voltage in your design
Voc - Array - HI Temp Compensated | 690.232
Vmp - Array - Non-TempCompen | 610
Vmp - Array - LO Temp Compensated | 682.59 | Use this Vmp value as working voltage in your design
Vmp - Array - HI Temp Compensated | 554.002
Vmp of Array | 610
FE recommended Vmp | 225
FE Portal Calculated Min Vmp | 190
Sum of PV Amps fr all Arrays Imp | 8.2
Max Increase in Imp @ max Temp | 1.62%
Temp Compensated Array Imp | 8.3328 | Use this Imp value as max PV current in your design

## CEP Models (hidden)
[10 empty] | Module Size (mm) |  |  | Width (mm) | Panel Hole
Panel Model | Wp | Type | Voc | Vmp | Imp | tcVoc | tcImp | Voc/cell | Vmp/cell | Height | Width | Thickness | Of 2 Holes | From Edge
CEP-100M/12 | 100 | Mono | 22.5 | 18.9 | 5.29 | -0.333 | 0.03 | 0.625 | 0.525 | 1195 | 541 | 35 | 491 | 25
CEP-150M/12 | 150 | Mono | 22.4 | 18.2 | 8.24 | -0.31 | 0.03 | 0.62222 | 0.50556 | 1482 | 676 | 35 | 626 | 25
CEP-240P-60 | 240 | Poly | 37.35 | 30.89 | 7.77 | -0.34 | 0.06 | 0.6225 | 0.51483 | 1650 | 992 | 40 | 942 | 25
CEP-250M-60 | 250 | Mono | 38 | 30.5 | 8.2 | -0.34 | 0.06 | 0.63333 | 0.50833 | 1650 | 992 | 40 | 942 | 25
CEP-250P-60 | 250 | Poly | 37.58 | 31.73 | 7.88 | -0.34 | 0.06 | 0.62633 | 0.52883 | 1650 | 992 | 40 | 942 | 25
CEP-80M/12 | 80 | Mono | 21.9 | 17.5 | 4.56 | -0.333 | 0.03 | 0.60833 | 0.48611 | 1195 | 541 | 35 | 491 | 25